## Slide 1
CLEAN ROOM MONITORING SYSTEM
SECOND REVISION

## Slide 2
POWER
Buck-Boost, output 3.3 V
Booster, output 5V
Main parts in system.
Power goes to sensors + components
Both accepts voltage range of:
1.8V - 5.5V.
Output => determined by the feedback resistors
R3 = R4(Vout/1 - Vfb), Vfb = 0.5V

## Slide 3
Previous schematic
USB CONNECTION
CANNOT UPLOAD CODE → PORT NOT SHOWING
POSSIBLE ISSUES:
      CABLE → X
      DRIVERS INSTALLATION → X
      ADDITIONAL LIBRARIES → X

## Slide 4
CP2102-GM
Data sheet
Previous schematic
Problem:
USB is only for uploading code, not supplying power
retrieved from:
https://www.silabs.com/documents/public/data-sheets/CP2102-9.pdf

## Slide 5
Data sheet
Current schematic
Fix:
A different USB_VBUS line,
self-powered system.
retrieved from:
https://www.silabs.com/documents/public/data-sheets/CP2102-9.pdf

## Slide 6
BOOT + RESET
How?
  Click Upload on Arduino
  Wait until you see:
Connecting...
  Perform the sequence:
    Hold BOOT
    Press and release RESET
    Release BOOT when you see “writing...”
Code Upload Problem?
Manually force ESP32 to enter bootloader mode to successfully upload code

## Slide 7
For all ESP modules, the reference image is recommended to enter boot loader mode.
Eliminates the need to manually press the BOOT and RESET buttons every time you upload code.
AUTO
PROGRAMMING
retrieved from:
https://docs.espressif.com/projects/esp-iot-solution/en/latest/hw-reference/ESP-Prog_guide.html
DTR
RTS
EN
IO0

## Slide 8
Schotky diodes determine the voltage through the intersection.
Higher voltage will pass.
POWER SUPPLY
Direct ~5V supplied to system
Initial stage and fully charged stage: still supplies voltage
Battery stops discharging at 3.0V to protect cell
BATTERY
Charges while DC is connected.
Supplies power once DC is disconnected, reliable in power outages.
3.0V - 4.2V discharge
DC JACK
Power Supply Architecture

## Slide 9
PCB BOARD
TEST PADS
Reset and Boot Buttons
Auto Programming
Alternative Wirings

## Slide 10
Extract of Arduino code
CODE + BLYNK
  CLEANED
  IMPROVED
  DEBUGGED
  REMOTE NOTIFICATION ENABLED WITH BLYNK.IO
NEXT PAGE

## Slide 12
FURTHE R STEPS
  CHECK HARDWARE
  UPLOAD CODE, RUN IT
  TEST SENSOR READINGS
  ENCLOSURE DESIGN FOR COMPONENTS